## clipping_test_a2750p
name | enabled | product | access_doc_addr | addr_doc | words | value_type | write_value | expected_value | valid_low | valid_high | read_doc_addr | read_value_type | commit_value | settle_ms | restore_value | restore_after | notes
테스트 케이스 이름 | TRUE/FALSE | 실행 UI 제품명. A2750P는 A2700 계열 모듈이므로 A2700 선택 기준 | setup access 문서 주소. 실행 시 내부에서 -1 적용 | 값을 write할 대상 문서 주소. 실행 시 내부에서 -1 적용 | Modbus word 수 | uint16/int16/uint32/int32/int64/float | 범위 밖으로 넣을 raw register 값 | 장치가 clipping 후 돌려줘야 하는 raw register 값 | 허용 최소 raw 값 | 허용 최대 raw 값 | readback 문서 주소. blank면 addr_doc 사용 | blank면 value_type 사용 | access commit 값. 보통 1 | commit 후 readback 전 대기 ms | 테스트 후 복구할 raw 값 | TRUE면 restore_value로 복구 | 설명/화면 표시 환산 메모
A2750_COMMON_UI_Accura_2750_Common_Interface_Event_LED_period_low_clip | TRUE | A2700 | 51222 | 51223 | 1 | uint16 | 1 | 2 | 2 | 50 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 713 ¦ A2750P/D/LC Event LED period 범위 : 2 ~ 50 (단위 : 0.1초) ¦ low clipping
A2750_COMMON_UI_Accura_2750_Common_Interface_Event_LED_period_high_clip | TRUE | A2700 | 51222 | 51223 | 1 | uint16 | 51 | 50 | 2 | 50 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 713 ¦ A2750P/D/LC Event LED period 범위 : 2 ~ 50 (단위 : 0.1초) ¦ high clipping
A2750_COMMON_UI_Accura_2750_Common_Interface_Event_LED_on_time_low_clip | TRUE | A2700 | 51222 | 51224 | 1 | uint16 | 0 | 1 | 1 | 50 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 714 ¦ A2700P/D/LC Event LED on time 범위 : 1 ~ 50 (단위 : 0.1초) ¦ low clipping
A2750_COMMON_UI_Accura_2750_Common_Interface_Event_LED_on_time_high_clip | TRUE | A2700 | 51222 | 51224 | 1 | uint16 | 51 | 50 | 1 | 50 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 714 ¦ A2700P/D/LC Event LED on time 범위 : 1 ~ 50 (단위 : 0.1초) ¦ high clipping
A2750_COMMON_UI_Accura_2750_Common_Interface_Comm_LED_period_low_clip | TRUE | A2700 | 51222 | 51225 | 1 | uint16 | 1 | 2 | 2 | 50 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 715 ¦ A2750P/D/LC Comm LED period 범위 : 2 ~ 50 (단위 : 0.1초) ¦ low clipping
A2750_COMMON_UI_Accura_2750_Common_Interface_Comm_LED_period_high_clip | TRUE | A2700 | 51222 | 51225 | 1 | uint16 | 51 | 50 | 2 | 50 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 715 ¦ A2750P/D/LC Comm LED period 범위 : 2 ~ 50 (단위 : 0.1초) ¦ high clipping
A2750_COMMON_UI_Accura_2750_Common_Interface_Comm_LED_on_time_low_clip | TRUE | A2700 | 51222 | 51226 | 1 | uint16 | 0 | 1 | 1 | 50 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 716 ¦ A2700P/D/LC Comm LED on time 범위 : 1 ~ 50 (단위 : 0.1초) ¦ low clipping
A2750_COMMON_UI_Accura_2750_Common_Interface_Comm_LED_on_time_high_clip | TRUE | A2700 | 51222 | 51226 | 1 | uint16 | 51 | 50 | 1 | 50 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 716 ¦ A2700P/D/LC Comm LED on time 범위 : 1 ~ 50 (단위 : 0.1초) ¦ high clipping
A2750_COMMON_UI_Accura_2750_Common_Interface_Alarm_LED_period_low_clip | TRUE | A2700 | 51222 | 51227 | 1 | uint16 | 1 | 2 | 2 | 50 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 717 ¦ A2750P/D/LC Alarm LED period 범위 : 2 ~ 50 (단위 : 0.1초) ¦ low clipping
A2750_COMMON_UI_Accura_2750_Common_Interface_Alarm_LED_period_high_clip | TRUE | A2700 | 51222 | 51227 | 1 | uint16 | 51 | 50 | 2 | 50 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 717 ¦ A2750P/D/LC Alarm LED period 범위 : 2 ~ 50 (단위 : 0.1초) ¦ high clipping
A2750_COMMON_UI_Accura_2750_Common_Interface_Alarm_LED_on_time_low_clip | TRUE | A2700 | 51222 | 51228 | 1 | uint16 | 0 | 1 | 1 | 50 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 718 ¦ A2700P/D/LC Alarm LED on time 범위 : 1 ~ 50 (단위 : 0.1초) ¦ low clipping
A2750_COMMON_UI_Accura_2750_Common_Interface_Alarm_LED_on_time_high_clip | TRUE | A2700 | 51222 | 51228 | 1 | uint16 | 51 | 50 | 1 | 50 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 718 ¦ A2700P/D/LC Alarm LED on time 범위 : 1 ~ 50 (단위 : 0.1초) ¦ high clipping
A2750_COMMON_UI_Accura_2750_Common_Interface_Fault_LED_period_low_clip | TRUE | A2700 | 51222 | 51229 | 1 | uint16 | 1 | 2 | 2 | 50 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 719 ¦ A2750P/D/LC Fault LED period 범위 : 2 ~ 50 (단위 : 0.1초) ¦ low clipping
A2750_COMMON_UI_Accura_2750_Common_Interface_Fault_LED_period_high_clip | TRUE | A2700 | 51222 | 51229 | 1 | uint16 | 51 | 50 | 2 | 50 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 719 ¦ A2750P/D/LC Fault LED period 범위 : 2 ~ 50 (단위 : 0.1초) ¦ high clipping
A2750_COMMON_UI_Accura_2750_Common_Interface_Fault_LED_on_time_low_clip | TRUE | A2700 | 51222 | 51230 | 1 | uint16 | 0 | 1 | 1 | 50 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 720 ¦ A2700P/D/LC Fault LED on time 범위 : 1 ~ 50 (단위 : 0.1초) ¦ low clipping
A2750_COMMON_UI_Accura_2750_Common_Interface_Fault_LED_on_time_high_clip | TRUE | A2700 | 51222 | 51230 | 1 | uint16 | 51 | 50 | 1 | 50 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 720 ¦ A2700P/D/LC Fault LED on time 범위 : 1 ~ 50 (단위 : 0.1초) ¦ high clipping
A2750_COMMON_UI_Accura_2750_Common_Interface_Device_LED_period_low_clip | TRUE | A2700 | 51222 | 51231 | 1 | uint16 | 1 | 2 | 2 | 50 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 721 ¦ A2750P/D/LC Device LED period 범위 : 2 ~ 50 (단위 : 0.1초) ¦ low clipping
A2750_COMMON_UI_Accura_2750_Common_Interface_Device_LED_period_high_clip | TRUE | A2700 | 51222 | 51231 | 1 | uint16 | 51 | 50 | 2 | 50 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 721 ¦ A2750P/D/LC Device LED period 범위 : 2 ~ 50 (단위 : 0.1초) ¦ high clipping
A2750_COMMON_UI_Accura_2750_Common_Interface_Device_LED_on_time_low_clip | TRUE | A2700 | 51222 | 51232 | 1 | uint16 | 0 | 1 | 1 | 50 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 722 ¦ A2700P/D/LC Device LED on time 범위 : 1 ~ 50 (단위 : 0.1초) ¦ low clipping
A2750_COMMON_UI_Accura_2750_Common_Interface_Device_LED_on_time_high_clip | TRUE | A2700 | 51222 | 51232 | 1 | uint16 | 51 | 50 | 1 | 50 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 722 ¦ A2700P/D/LC Device LED on time 범위 : 1 ~ 50 (단위 : 0.1초) ¦ high clipping
A2750_COMMON_UI_Accura_2750_Common_Interface_Control_button_time_delay_of_A2750_low_clip | TRUE | A2700 | 51222 | 51233 | 1 | uint16 | 99 | 100 | 100 | 5000 |  |  | 1 | 500 | 1000 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 723 ¦ Motor control button time delay 100 ~ 5000 ¦ low clipping
A2750_COMMON_UI_Accura_2750_Common_Interface_Control_button_time_delay_of_A2750_high_clip | TRUE | A2700 | 51222 | 51233 | 1 | uint16 | 5001 | 5000 | 100 | 5000 |  |  | 1 | 500 | 1000 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 723 ¦ Motor control button time delay 100 ~ 5000 ¦ high clipping
A2750_COMMON_UI_Accura_2750_Common_Interface_STOP_extension_time_high_clip | TRUE | A2700 | 51222 | 51236 | 1 | uint16 | 21 | 20 | 0 | 20 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51221 must be preset before run ¦ access doc addr 51222 ¦ source map row 726 ¦ STOP extension time 범위 : 0 ~ 20 (단위 : 0.1초) ¦ high clipping
A2750P_UI_Accura_2750P_User_Interface_LCD_Backlight_Timeout_low_clip | TRUE | A2700 | 51242 | 51243 | 1 | uint16 | 29 | 30 | 30 | 999 |  |  | 1 | 500 | 60 | TRUE | A2750P ID=1 assumed; ID doc addr 51241 must be preset before run ¦ access doc addr 51242 ¦ source map row 731 ¦ LCD Backlight Timeout 30 ~ 999 ¦ low clipping
A2750P_UI_Accura_2750P_User_Interface_LCD_Backlight_Timeout_high_clip | TRUE | A2700 | 51242 | 51243 | 1 | uint16 | 1000 | 999 | 30 | 999 |  |  | 1 | 500 | 60 | TRUE | A2750P ID=1 assumed; ID doc addr 51241 must be preset before run ¦ access doc addr 51242 ¦ source map row 731 ¦ LCD Backlight Timeout 30 ~ 999 ¦ high clipping
A2750P_UI_Accura_2750P_User_Interface_Setup_exit_timeout_low_clip | TRUE | A2700 | 51242 | 51244 | 1 | uint16 | 4 | 5 | 5 | 60 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51241 must be preset before run ¦ access doc addr 51242 ¦ source map row 732 ¦ Setup exit timeout 5 ~ 60 ¦ low clipping
A2750P_UI_Accura_2750P_User_Interface_Setup_exit_timeout_high_clip | TRUE | A2700 | 51242 | 51244 | 1 | uint16 | 61 | 60 | 5 | 60 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51241 must be preset before run ¦ access doc addr 51242 ¦ source map row 732 ¦ Setup exit timeout 5 ~ 60 ¦ high clipping
A2750P_MEAS_A2750P_Measurement_Setup_CT_Primary_current_low_clip | TRUE | A2700 | 51392 | 51396 | 2 | uint32 | 9 | 10 | 10 | 99999 |  |  | 1 | 500 | 50 | TRUE | A2750P ID=1 assumed; ID doc addr 51391 must be preset before run ¦ access doc addr 51392 ¦ source map row 791 ¦ 1차 전류 10(1.0A) ~ 99999(9999.9A) ¦ low clipping
A2750P_MEAS_A2750P_Measurement_Setup_CT_Primary_current_high_clip | TRUE | A2700 | 51392 | 51396 | 2 | uint32 | 100000 | 99999 | 10 | 99999 |  |  | 1 | 500 | 50 | TRUE | A2750P ID=1 assumed; ID doc addr 51391 must be preset before run ¦ access doc addr 51392 ¦ source map row 791 ¦ 1차 전류 10(1.0A) ~ 99999(9999.9A) ¦ high clipping
A2750P_MEAS_A2750P_Measurement_Setup_CT_Secondary_current_low_clip | TRUE | A2700 | 51392 | 51398 | 1 | uint16 | 9 | 10 | 10 | 50 |  |  | 1 | 500 | 50 | TRUE | A2750P ID=1 assumed; ID doc addr 51391 must be preset before run ¦ access doc addr 51392 ¦ source map row 792 ¦ 2차 전류 10(1.0A) ~ 50(5.0A) ¦ low clipping
A2750P_MEAS_A2750P_Measurement_Setup_CT_Secondary_current_high_clip | TRUE | A2700 | 51392 | 51398 | 1 | uint16 | 51 | 50 | 10 | 50 |  |  | 1 | 500 | 50 | TRUE | A2750P ID=1 assumed; ID doc addr 51391 must be preset before run ¦ access doc addr 51392 ¦ source map row 792 ¦ 2차 전류 10(1.0A) ~ 50(5.0A) ¦ high clipping
A2750P_MEAS_A2750P_Measurement_Setup_Minimum_measured_ZCT_current_low_clip | TRUE | A2700 | 51392 | 51403 | 1 | uint16 | 0 | 1 | 1 | 100 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51391 must be preset before run ¦ access doc addr 51392 ¦ source map row 797 ¦ ZCT 최소 계측 전류 1 ~ 100 ¦ low clipping
A2750P_MEAS_A2750P_Measurement_Setup_Minimum_measured_ZCT_current_high_clip | TRUE | A2700 | 51392 | 51403 | 1 | uint16 | 101 | 100 | 1 | 100 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51391 must be preset before run ¦ access doc addr 51392 ¦ source map row 797 ¦ ZCT 최소 계측 전류 1 ~ 100 ¦ high clipping
A2750P_MEAS_A2750P_Measurement_Setup_Start_to_run_threshold_low_clip | TRUE | A2700 | 51392 | 51405 | 1 | uint16 | 99 | 100 | 100 | 800 |  |  | 1 | 500 | 100 | TRUE | A2750P ID=1 assumed; ID doc addr 51391 must be preset before run ¦ access doc addr 51392 ¦ source map row 799 ¦ Motor start 와 run 판단 기준. 100 ~ 800 ¦ low clipping
A2750P_MEAS_A2750P_Measurement_Setup_Start_to_run_threshold_high_clip | TRUE | A2700 | 51392 | 51405 | 1 | uint16 | 801 | 800 | 100 | 800 |  |  | 1 | 500 | 100 | TRUE | A2750P ID=1 assumed; ID doc addr 51391 must be preset before run ¦ access doc addr 51392 ¦ source map row 799 ¦ Motor start 와 run 판단 기준. 100 ~ 800 ¦ high clipping
A2750P_MEAS_A2750P_Measurement_Setup_Start_to_run_time_delay_low_clip | TRUE | A2700 | 51392 | 51406 | 1 | uint16 | 0 | 1 | 1 | 500 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51391 must be preset before run ¦ access doc addr 51392 ¦ source map row 800 ¦ 판단 지연 시간 1 ~ 500 ¦ low clipping
A2750P_MEAS_A2750P_Measurement_Setup_Start_to_run_time_delay_high_clip | TRUE | A2700 | 51392 | 51406 | 1 | uint16 | 501 | 500 | 1 | 500 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51391 must be preset before run ¦ access doc addr 51392 ¦ source map row 800 ¦ 판단 지연 시간 1 ~ 500 ¦ high clipping
A2750P_MEAS_A2750P_Measurement_Setup_A2750INV_PT_Primary_Voltage_low_clip | TRUE | A2700 | 51392 | 51409 | 2 | uint32 | 0 | 1 | 1 | 999999 |  |  | 1 | 500 | 3800 | TRUE | A2750P ID=1 assumed; ID doc addr 51391 must be preset before run ¦ access doc addr 51392 ¦ source map row 803 ¦ 1차 전압 1(0.1V) ~ 999999(99999.9V) ¦ low clipping
A2750P_MEAS_A2750P_Measurement_Setup_A2750INV_PT_Primary_Voltage_high_clip | TRUE | A2700 | 51392 | 51409 | 2 | uint32 | 1000000 | 999999 | 1 | 999999 |  |  | 1 | 500 | 3800 | TRUE | A2750P ID=1 assumed; ID doc addr 51391 must be preset before run ¦ access doc addr 51392 ¦ source map row 803 ¦ 1차 전압 1(0.1V) ~ 999999(99999.9V) ¦ high clipping
A2750P_MEAS_A2750P_Measurement_Setup_A2750INV_PT_Secondary_Voltage_low_clip | TRUE | A2700 | 51392 | 51411 | 1 | uint16 | 0 | 1 | 1 | 9999 |  |  | 1 | 500 | 3800 | TRUE | A2750P ID=1 assumed; ID doc addr 51391 must be preset before run ¦ access doc addr 51392 ¦ source map row 804 ¦ 2차 전압 1(0.1V) ~ 9999(999.9V) ¦ low clipping
A2750P_MEAS_A2750P_Measurement_Setup_A2750INV_PT_Secondary_Voltage_high_clip | TRUE | A2700 | 51392 | 51411 | 1 | uint16 | 10000 | 9999 | 1 | 9999 |  |  | 1 | 500 | 3800 | TRUE | A2750P ID=1 assumed; ID doc addr 51391 must be preset before run ¦ access doc addr 51392 ¦ source map row 804 ¦ 2차 전압 1(0.1V) ~ 9999(999.9V) ¦ high clipping
A2750P_MEAS_A2750P_Measurement_Setup_A2750INV_Minimum_measured_secondary_voltage_low_clip | TRUE | A2700 | 51392 | 51412 | 1 | uint16 | 0 | 1 | 1 | 20 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51391 must be preset before run ¦ access doc addr 51392 ¦ source map row 805 ¦ PT 2차측 최소 계측 전압 1 ~ 20 V ¦ low clipping
A2750P_MEAS_A2750P_Measurement_Setup_A2750INV_Minimum_measured_secondary_voltage_high_clip | TRUE | A2700 | 51392 | 51412 | 1 | uint16 | 21 | 20 | 1 | 20 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51391 must be preset before run ¦ access doc addr 51392 ¦ source map row 805 ¦ PT 2차측 최소 계측 전압 1 ~ 20 V ¦ high clipping
A2750P_PROT_THR_Alarm_threshold_low_clip | TRUE | A2700 | 51542 | 51545 | 1 | uint16 | 9 | 10 | 10 | 100 |  |  | 1 | 500 | 80 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 821 ¦ 알람 기준치 범위 (TCU 기준) : 10 ~ 100 ¦ low clipping
A2750P_PROT_THR_Alarm_threshold_high_clip | TRUE | A2700 | 51542 | 51545 | 1 | uint16 | 101 | 100 | 10 | 100 |  |  | 1 | 500 | 80 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 821 ¦ 알람 기준치 범위 (TCU 기준) : 10 ~ 100 ¦ high clipping
A2750P_PROT_THR_Motor_trip_class_low_clip | TRUE | A2700 | 51542 | 51546 | 1 | uint16 | 4 | 5 | 5 | 40 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 822 ¦ Motor trip class 5 ~ 40 ¦ low clipping
A2750P_PROT_THR_Motor_trip_class_high_clip | TRUE | A2700 | 51542 | 51546 | 1 | uint16 | 41 | 40 | 5 | 40 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 822 ¦ Motor trip class 5 ~ 40 ¦ high clipping
A2750P_PROT_THR_Service_factor_low_clip | TRUE | A2700 | 51542 | 51547 | 1 | uint16 | 99 | 100 | 100 | 200 |  |  | 1 | 500 | 115 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 823 ¦ Service factor 100(1.00) ~ 200(2.00) ¦ low clipping
A2750P_PROT_THR_Service_factor_high_clip | TRUE | A2700 | 51542 | 51547 | 1 | uint16 | 201 | 200 | 100 | 200 |  |  | 1 | 500 | 115 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 823 ¦ Service factor 100(1.00) ~ 200(2.00) ¦ high clipping
A2750P_PROT_THR_Current_unbalance_factor_high_clip | TRUE | A2700 | 51542 | 51548 | 1 | uint16 | 101 | 100 | 0 | 100 |  |  | 1 | 500 | 0 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 824 ¦ Current unabalance factor 0(0.0) ~ 100(10.0) ¦ high clipping
A2750P_PROT_THR_Fault_reset_timeout_low_clip | TRUE | A2700 | 51542 | 51551 | 1 | uint16 | 59 | 60 | 60 | 9999 |  |  | 1 | 500 | 300 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 827 ¦ Fault reset 시간. Cooling mode가 Time으로 설정된 경우에만 사용 60 ~ 9999 ¦ low clipping
A2750P_PROT_THR_Fault_reset_timeout_high_clip | TRUE | A2700 | 51542 | 51551 | 1 | uint16 | 10000 | 9999 | 60 | 9999 |  |  | 1 | 500 | 300 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 827 ¦ Fault reset 시간. Cooling mode가 Time으로 설정된 경우에만 사용 60 ~ 9999 ¦ high clipping
A2750P_PROT_THR_Pause_time_high_clip | TRUE | A2700 | 51542 | 51552 | 1 | uint16 | 10000 | 9999 | 0 | 9999 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 828 ¦ Pause time. Cooling mode가 Time으로 설정된 경우에만 사용 0 ~ 9999 ¦ high clipping
A2750P_PROT_THR_Restart_level_low_clip | TRUE | A2700 | 51542 | 51553 | 1 | uint16 | 9 | 10 | 10 | 100 |  |  | 1 | 500 | 80 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 829 ¦ Restart level. Cooling mode가 Restart level인 경우에만 사용 10 ~ 100 ¦ low clipping
A2750P_PROT_THR_Restart_level_high_clip | TRUE | A2700 | 51542 | 51553 | 1 | uint16 | 101 | 100 | 10 | 100 |  |  | 1 | 500 | 80 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 829 ¦ Restart level. Cooling mode가 Restart level인 경우에만 사용 10 ~ 100 ¦ high clipping
A2750P_PROT_OCR_Alarm_threshold_low_clip | TRUE | A2700 | 51542 | 51558 | 1 | uint16 | 89 | 90 | 90 | 600 |  |  | 1 | 500 | 200 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 834 ¦ Alarm 기준 90 ~ 600 ¦ low clipping
A2750P_PROT_OCR_Alarm_threshold_high_clip | TRUE | A2700 | 51542 | 51558 | 1 | uint16 | 601 | 600 | 90 | 600 |  |  | 1 | 500 | 200 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 834 ¦ Alarm 기준 90 ~ 600 ¦ high clipping
A2750P_PROT_OCR_Alarm_time_delay_low_clip | TRUE | A2700 | 51542 | 51559 | 1 | uint16 | 4 | 5 | 5 | 9999 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 835 ¦ Alarm 판단 지연 시간 5(0.05sec) ~ 9999(99.99sec) ¦ low clipping
A2750P_PROT_OCR_Alarm_time_delay_high_clip | TRUE | A2700 | 51542 | 51559 | 1 | uint16 | 10000 | 9999 | 5 | 9999 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 835 ¦ Alarm 판단 지연 시간 5(0.05sec) ~ 9999(99.99sec) ¦ high clipping
A2750P_PROT_POCR_Fault_threshold_low_clip | TRUE | A2700 | 51542 | 51562 | 1 | uint16 | 69 | 70 | 70 | 90 |  |  | 1 | 500 | 80 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 838 ¦ Fault 기준 70 ~ 90 ¦ low clipping
A2750P_PROT_POCR_Fault_threshold_high_clip | TRUE | A2700 | 51542 | 51562 | 1 | uint16 | 91 | 90 | 70 | 90 |  |  | 1 | 500 | 80 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 838 ¦ Fault 기준 70 ~ 90 ¦ high clipping
A2750P_PROT_POCR_Fault_time_delay_low_clip | TRUE | A2700 | 51542 | 51563 | 1 | uint16 | 4 | 5 | 5 | 5000 |  |  | 1 | 500 | 500 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 839 ¦ Fault 판단 지연 시간 5(0.05sec) ~ 5000(50.00sec) ¦ low clipping
A2750P_PROT_POCR_Fault_time_delay_high_clip | TRUE | A2700 | 51542 | 51563 | 1 | uint16 | 5001 | 5000 | 5 | 5000 |  |  | 1 | 500 | 500 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 839 ¦ Fault 판단 지연 시간 5(0.05sec) ~ 5000(50.00sec) ¦ high clipping
A2750P_PROT_POCR_Alarm_threshold_low_clip | TRUE | A2700 | 51542 | 51564 | 1 | uint16 | 69 | 70 | 70 | 90 |  |  | 1 | 500 | 80 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 840 ¦ Alarm 기준 70 ~ 90 ¦ low clipping
A2750P_PROT_POCR_Alarm_threshold_high_clip | TRUE | A2700 | 51542 | 51564 | 1 | uint16 | 91 | 90 | 70 | 90 |  |  | 1 | 500 | 80 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 840 ¦ Alarm 기준 70 ~ 90 ¦ high clipping
A2750P_PROT_POCR_Startup_time_delay_high_clip | TRUE | A2700 | 51542 | 51565 | 1 | uint16 | 51 | 50 | 0 | 50 |  |  | 1 | 500 | 0 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 841 ¦ Startup 지연 시간 0(0.0ec) ~ 50(5.0sec) ¦ high clipping
A2750P_PROT_UBCR_Fault_threshold_low_clip | TRUE | A2700 | 51542 | 51570 | 1 | uint16 | 9 | 10 | 10 | 70 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 846 ¦ Fault 기준 10 ~ 70 ¦ low clipping
A2750P_PROT_UBCR_Fault_threshold_high_clip | TRUE | A2700 | 51542 | 51570 | 1 | uint16 | 71 | 70 | 10 | 70 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 846 ¦ Fault 기준 10 ~ 70 ¦ high clipping
A2750P_PROT_UBCR_Fault_time_delay_low_clip | TRUE | A2700 | 51542 | 51571 | 1 | uint16 | 9 | 10 | 10 | 5000 |  |  | 1 | 500 | 500 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 847 ¦ Fault 판단 지연 시간 10(0.10sec) ~ 5000(50.00sec) ¦ low clipping
A2750P_PROT_UBCR_Fault_time_delay_high_clip | TRUE | A2700 | 51542 | 51571 | 1 | uint16 | 5001 | 5000 | 10 | 5000 |  |  | 1 | 500 | 500 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 847 ¦ Fault 판단 지연 시간 10(0.10sec) ~ 5000(50.00sec) ¦ high clipping
A2750P_PROT_UBCR_Alarm_threshold_low_clip | TRUE | A2700 | 51542 | 51572 | 1 | uint16 | 9 | 10 | 10 | 70 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 848 ¦ Alarm 기준 10 ~ 70 ¦ low clipping
A2750P_PROT_UBCR_Alarm_threshold_high_clip | TRUE | A2700 | 51542 | 51572 | 1 | uint16 | 71 | 70 | 10 | 70 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 848 ¦ Alarm 기준 10 ~ 70 ¦ high clipping
A2750P_PROT_UBCR_Alarm_time_delay_low_clip | TRUE | A2700 | 51542 | 51573 | 1 | uint16 | 4 | 5 | 5 | 9999 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 849 ¦ Alarm 판단 지연 시간 5(0.05sec) ~ 9999(99.99sec) ¦ low clipping
A2750P_PROT_UBCR_Alarm_time_delay_high_clip | TRUE | A2700 | 51542 | 51573 | 1 | uint16 | 10000 | 9999 | 5 | 9999 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 849 ¦ Alarm 판단 지연 시간 5(0.05sec) ~ 9999(99.99sec) ¦ high clipping
A2750P_PROT_UBCR_Startup_time_delay_high_clip | TRUE | A2700 | 51542 | 51574 | 1 | uint16 | 51 | 50 | 0 | 50 |  |  | 1 | 500 | 0 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 850 ¦ Startup 지연 시간 0(0.0ec) ~ 50(5.0sec) ¦ high clipping
A2750P_PROT_JAM_Fault_threshold_low_clip | TRUE | A2700 | 51542 | 51579 | 1 | uint16 | 99 | 100 | 100 | 800 |  |  | 1 | 500 | 200 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 855 ¦ Fault 기준 100 ~ 800 ¦ low clipping
A2750P_PROT_JAM_Fault_threshold_high_clip | TRUE | A2700 | 51542 | 51579 | 1 | uint16 | 801 | 800 | 100 | 800 |  |  | 1 | 500 | 200 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 855 ¦ Fault 기준 100 ~ 800 ¦ high clipping
A2750P_PROT_JAM_Fault_time_delay_low_clip | TRUE | A2700 | 51542 | 51580 | 1 | uint16 | 0 | 1 | 1 | 500 |  |  | 1 | 500 | 1 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 856 ¦ Fault 판단 지연 시간 1 ~ 500 ¦ low clipping
A2750P_PROT_JAM_Fault_time_delay_high_clip | TRUE | A2700 | 51542 | 51580 | 1 | uint16 | 501 | 500 | 1 | 500 |  |  | 1 | 500 | 1 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 856 ¦ Fault 판단 지연 시간 1 ~ 500 ¦ high clipping
A2750P_PROT_JAM_Alarm_threshold_low_clip | TRUE | A2700 | 51542 | 51581 | 1 | uint16 | 99 | 100 | 100 | 800 |  |  | 1 | 500 | 200 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 857 ¦ Alarm 기준 100 ~ 800 ¦ low clipping
A2750P_PROT_JAM_Alarm_threshold_high_clip | TRUE | A2700 | 51542 | 51581 | 1 | uint16 | 801 | 800 | 100 | 800 |  |  | 1 | 500 | 200 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 857 ¦ Alarm 기준 100 ~ 800 ¦ high clipping
A2750P_PROT_JAM_Alarm_time_delay_low_clip | TRUE | A2700 | 51542 | 51582 | 1 | uint16 | 4 | 5 | 5 | 9999 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 858 ¦ Alarm 판단 지연 시간 5(0.05sec) ~ 9999(99.99sec) ¦ low clipping
A2750P_PROT_JAM_Alarm_time_delay_high_clip | TRUE | A2700 | 51542 | 51582 | 1 | uint16 | 10000 | 9999 | 5 | 9999 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 858 ¦ Alarm 판단 지연 시간 5(0.05sec) ~ 9999(99.99sec) ¦ high clipping
A2750P_PROT_GR_ZCT_Fault_threshold_low_clip | TRUE | A2700 | 51542 | 51586 | 1 | uint16 | 1 | 2 | 2 | 2000 |  |  | 1 | 500 | 100 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 862 ¦ Fault 기준 2(0.02A) ~ 2000(20.00A) ¦ low clipping
A2750P_PROT_GR_ZCT_Fault_threshold_high_clip | TRUE | A2700 | 51542 | 51586 | 1 | uint16 | 2001 | 2000 | 2 | 2000 |  |  | 1 | 500 | 100 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 862 ¦ Fault 기준 2(0.02A) ~ 2000(20.00A) ¦ high clipping
A2750P_PROT_GR_ZCT_Fault_time_delay_low_clip | TRUE | A2700 | 51542 | 51587 | 1 | uint16 | 4 | 5 | 5 | 5000 |  |  | 1 | 500 | 100 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 863 ¦ Fault 판단 지연 시간 5(0.05sec) ~ 5000(50.00sec) ¦ low clipping
A2750P_PROT_GR_ZCT_Fault_time_delay_high_clip | TRUE | A2700 | 51542 | 51587 | 1 | uint16 | 5001 | 5000 | 5 | 5000 |  |  | 1 | 500 | 100 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 863 ¦ Fault 판단 지연 시간 5(0.05sec) ~ 5000(50.00sec) ¦ high clipping
A2750P_PROT_GR_ZCT_Alarm_threshold_low_clip | TRUE | A2700 | 51542 | 51588 | 1 | uint16 | 1 | 2 | 2 | 2000 |  |  | 1 | 500 | 100 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 864 ¦ Alarm 기준 2(0.02A) ~ 2000(20.00A) ¦ low clipping
A2750P_PROT_GR_ZCT_Alarm_threshold_high_clip | TRUE | A2700 | 51542 | 51588 | 1 | uint16 | 2001 | 2000 | 2 | 2000 |  |  | 1 | 500 | 100 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 864 ¦ Alarm 기준 2(0.02A) ~ 2000(20.00A) ¦ high clipping
A2750P_PROT_GR_ZCT_Alarm_time_delay_low_clip | TRUE | A2700 | 51542 | 51589 | 1 | uint16 | 4 | 5 | 5 | 9999 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 865 ¦ Alarm 판단 지연 시간 5(0.05sec) ~ 9999(99.99sec) ¦ low clipping
A2750P_PROT_GR_ZCT_Alarm_time_delay_high_clip | TRUE | A2700 | 51542 | 51589 | 1 | uint16 | 10000 | 9999 | 5 | 9999 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 865 ¦ Alarm 판단 지연 시간 5(0.05sec) ~ 9999(99.99sec) ¦ high clipping
A2750P_PROT_GR_ZCT_Startup_time_delay_low_clip | FALSE | A2700 | 51542 | 51591 | 1 | uint16 | 0 | 1 | 1 | 500 |  |  | 1 | 500 | 1 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 867 ¦ Startup 지연 시간 0: Auto, 1(0.1sec) ~ 500(50.0sec) ¦ low clipping
A2750P_PROT_GR_ZCT_Startup_time_delay_high_clip | TRUE | A2700 | 51542 | 51591 | 1 | uint16 | 501 | 500 | 1 | 500 |  |  | 1 | 500 | 0 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 867 ¦ Startup 지연 시간 0: Auto, 1(0.1sec) ~ 500(50.0sec) ¦ high clipping
A2750P_PROT_GR_CT_Fault_time_delay_low_clip | TRUE | A2700 | 51542 | 51595 | 1 | uint16 | 4 | 5 | 5 | 5000 |  |  | 1 | 500 | 100 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 871 ¦ Fault 판단 지연 시간 5(0.05sec) ~ 5000(50.00sec) ¦ low clipping
A2750P_PROT_GR_CT_Fault_time_delay_high_clip | TRUE | A2700 | 51542 | 51595 | 1 | uint16 | 5001 | 5000 | 5 | 5000 |  |  | 1 | 500 | 100 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 871 ¦ Fault 판단 지연 시간 5(0.05sec) ~ 5000(50.00sec) ¦ high clipping
A2750P_PROT_GR_CT_Alarm_time_delay_low_clip | TRUE | A2700 | 51542 | 51597 | 1 | uint16 | 4 | 5 | 5 | 9999 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 873 ¦ Alarm 판단 지연 시간 5(0.05sec) ~ 9999(99.99sec) ¦ low clipping
A2750P_PROT_GR_CT_Alarm_time_delay_high_clip | TRUE | A2700 | 51542 | 51597 | 1 | uint16 | 10000 | 9999 | 5 | 9999 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 873 ¦ Alarm 판단 지연 시간 5(0.05sec) ~ 9999(99.99sec) ¦ high clipping
A2750P_PROT_GR_CT_Startup_time_delay_low_clip | FALSE | A2700 | 51542 | 51599 | 1 | uint16 | 0 | 1 | 1 | 500 |  |  | 1 | 500 | 1 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 875 ¦ Startup 지연 시간 0 : Auto 1(0.1sec) ~ 500(50.0sec) ¦ low clipping
A2750P_PROT_GR_CT_Startup_time_delay_high_clip | TRUE | A2700 | 51542 | 51599 | 1 | uint16 | 501 | 500 | 1 | 500 |  |  | 1 | 500 | 0 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 875 ¦ Startup 지연 시간 0 : Auto 1(0.1sec) ~ 500(50.0sec) ¦ high clipping
A2750P_PROT_UCR_Fault_threshold_low_clip | TRUE | A2700 | 51542 | 51602 | 1 | uint16 | 9 | 10 | 10 | 90 |  |  | 1 | 500 | 50 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 878 ¦ Fault 기준 10 ~ 90 ¦ low clipping
A2750P_PROT_UCR_Fault_threshold_high_clip | TRUE | A2700 | 51542 | 51602 | 1 | uint16 | 91 | 90 | 10 | 90 |  |  | 1 | 500 | 50 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 878 ¦ Fault 기준 10 ~ 90 ¦ high clipping
A2750P_PROT_UCR_Fault_time_delay_low_clip | TRUE | A2700 | 51542 | 51603 | 1 | uint16 | 0 | 1 | 1 | 999 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 879 ¦ Fault 판단 지연 시간 1 ~ 999 ¦ low clipping
A2750P_PROT_UCR_Fault_time_delay_high_clip | TRUE | A2700 | 51542 | 51603 | 1 | uint16 | 1000 | 999 | 1 | 999 |  |  | 1 | 500 | 10 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 879 ¦ Fault 판단 지연 시간 1 ~ 999 ¦ high clipping
A2750P_PROT_UCR_Alarm_threshold_low_clip | TRUE | A2700 | 51542 | 51604 | 1 | uint16 | 9 | 10 | 10 | 90 |  |  | 1 | 500 | 50 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 880 ¦ Alarm 기준 10 ~ 90 ¦ low clipping
A2750P_PROT_UCR_Alarm_threshold_high_clip | TRUE | A2700 | 51542 | 51604 | 1 | uint16 | 91 | 90 | 10 | 90 |  |  | 1 | 500 | 50 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 880 ¦ Alarm 기준 10 ~ 90 ¦ high clipping
A2750P_PROT_UCR_Alarm_time_delay_low_clip | TRUE | A2700 | 51542 | 51605 | 1 | uint16 | 4 | 5 | 5 | 9999 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 881 ¦ Alarm 판단 지연 시간 5(0.05sec) ~ 9999(99.99sec) ¦ low clipping
A2750P_PROT_UCR_Alarm_time_delay_high_clip | TRUE | A2700 | 51542 | 51605 | 1 | uint16 | 10000 | 9999 | 5 | 9999 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 881 ¦ Alarm 판단 지연 시간 5(0.05sec) ~ 9999(99.99sec) ¦ high clipping
A2750P_PROT_MC_Supervision_Fault_threshold_low_clip | TRUE | A2700 | 51542 | 51609 | 1 | uint16 | 4 | 5 | 5 | 120 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 885 ¦ Fault 기준 5 ~ 120 ¦ low clipping
A2750P_PROT_MC_Supervision_Fault_threshold_high_clip | TRUE | A2700 | 51542 | 51609 | 1 | uint16 | 121 | 120 | 5 | 120 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 885 ¦ Fault 기준 5 ~ 120 ¦ high clipping
A2750P_PROT_MC_Supervision_Fault_time_delay_low_clip | TRUE | A2700 | 51542 | 51610 | 1 | uint16 | 0 | 1 | 1 | 100 |  |  | 1 | 500 | 20 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 886 ¦ Fault 판단 지연 시간 1(0.1 sec) ~ 100(10.0sec) ¦ low clipping
A2750P_PROT_MC_Supervision_Fault_time_delay_high_clip | TRUE | A2700 | 51542 | 51610 | 1 | uint16 | 101 | 100 | 1 | 100 |  |  | 1 | 500 | 20 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 886 ¦ Fault 판단 지연 시간 1(0.1 sec) ~ 100(10.0sec) ¦ high clipping
A2750P_PROT_IOCR_Fault_time_delay_low_clip | FALSE | A2700 | 51542 | 51613 | 1 | uint16 | 0 | 1 | 1 | 100 |  |  | 1 | 500 | 1 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 889 ¦ Fault 판단 지연 시간 정한시 : 1(0.1 sec) ~ 100(10.0sec) 순시 : 0 ※ ACB 는 0으로 고정 ¦ low clipping
A2750P_PROT_IOCR_Fault_time_delay_high_clip | TRUE | A2700 | 51542 | 51613 | 1 | uint16 | 101 | 100 | 1 | 100 |  |  | 1 | 500 | 0 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 889 ¦ Fault 판단 지연 시간 정한시 : 1(0.1 sec) ~ 100(10.0sec) 순시 : 0 ※ ACB 는 0으로 고정 ¦ high clipping
A2750P_PROT_PSR_Fault_threshold_low_clip | TRUE | A2700 | 51542 | 51614 | 1 | uint16 | 99 | 100 | 100 | 1000 |  |  | 1 | 500 | 200 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 890 ¦ Fault threshold. 100(100%) ~ 1000(1000%) UB2 : 역상분 불평형율 ¦ low clipping
A2750P_PROT_PSR_Fault_threshold_high_clip | TRUE | A2700 | 51542 | 51614 | 1 | uint16 | 1001 | 1000 | 100 | 1000 |  |  | 1 | 500 | 200 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 890 ¦ Fault threshold. 100(100%) ~ 1000(1000%) UB2 : 역상분 불평형율 ¦ high clipping
A2750P_PROT_PSR_Fault_delay_low_clip | TRUE | A2700 | 51542 | 51616 | 1 | uint16 | 4 | 5 | 5 | 200 |  |  | 1 | 500 | 20 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 892 ¦ Fault delay 5(0.05 sec) ~ 200(2.00 sec) ¦ low clipping
A2750P_PROT_PSR_Fault_delay_high_clip | TRUE | A2700 | 51542 | 51616 | 1 | uint16 | 201 | 200 | 5 | 200 |  |  | 1 | 500 | 20 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 892 ¦ Fault delay 5(0.05 sec) ~ 200(2.00 sec) ¦ high clipping
A2750P_PROT_UVR_Fault_delay_time_low_clip | TRUE | A2700 | 51542 | 51620 | 1 | uint16 | 1 | 2 | 2 | 250 |  |  | 1 | 500 | 30 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 896 ¦ Fault 판단 지연 시간 2(0.2sec) ~ 250(25.0sec) ¦ low clipping
A2750P_PROT_UVR_Fault_delay_time_high_clip | TRUE | A2700 | 51542 | 51620 | 1 | uint16 | 251 | 250 | 2 | 250 |  |  | 1 | 500 | 30 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 896 ¦ Fault 판단 지연 시간 2(0.2sec) ~ 250(25.0sec) ¦ high clipping
A2750P_PROT_UVR_Alarm_delay_time_low_clip | TRUE | A2700 | 51542 | 51622 | 1 | uint16 | 1 | 2 | 2 | 250 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 898 ¦ Alarm 판단 지연 시간 2(0.5sec) ~ 250(25.0sec) ¦ low clipping
A2750P_PROT_UVR_Alarm_delay_time_high_clip | TRUE | A2700 | 51542 | 51622 | 1 | uint16 | 251 | 250 | 2 | 250 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 898 ¦ Alarm 판단 지연 시간 2(0.5sec) ~ 250(25.0sec) ¦ high clipping
A2750P_PROT_LT_OCR_Fault_Threshold_low_clip | TRUE | A2700 | 51542 | 51624 | 1 | uint16 | 79 | 80 | 80 | 110 |  |  | 1 | 500 | 100 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 900 ¦ 80 ~ 110 (%FLC) ¦ low clipping
A2750P_PROT_LT_OCR_Fault_Threshold_high_clip | TRUE | A2700 | 51542 | 51624 | 1 | uint16 | 111 | 110 | 80 | 110 |  |  | 1 | 500 | 100 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 900 ¦ 80 ~ 110 (%FLC) ¦ high clipping
A2750P_PROT_LT_OCR_Fault_Delay_time_low_clip | TRUE | A2700 | 51542 | 51625 | 1 | uint16 | 49 | 50 | 50 | 3000 |  |  | 1 | 500 | 50 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 901 ¦ 50(0.5s) ~ 3000(30.00s) ¦ low clipping
A2750P_PROT_LT_OCR_Fault_Delay_time_high_clip | TRUE | A2700 | 51542 | 51625 | 1 | uint16 | 3001 | 3000 | 50 | 3000 |  |  | 1 | 500 | 50 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 901 ¦ 50(0.5s) ~ 3000(30.00s) ¦ high clipping
A2750P_PROT_I_OCR_extension_I_OCR_Alarm_Delay_Time_low_clip | FALSE | A2700 | 51542 | 51629 | 1 | uint16 | 0 | 1 | 1 | 100 |  |  | 1 | 500 | 1 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 905 ¦ Alarm 판단 지연 시간 정한시 : 1(0.1 sec) ~ 100(10.0sec) 순시 : 0 ※ ACB 는 0으로 고정 ¦ low clipping
A2750P_PROT_I_OCR_extension_I_OCR_Alarm_Delay_Time_high_clip | TRUE | A2700 | 51542 | 51629 | 1 | uint16 | 101 | 100 | 1 | 100 |  |  | 1 | 500 | 0 | TRUE | A2750P ID=1 assumed; ID doc addr 51541 must be preset before run ¦ access doc addr 51542 ¦ source map row 905 ¦ Alarm 판단 지연 시간 정한시 : 1(0.1 sec) ~ 100(10.0sec) 순시 : 0 ※ ACB 는 0으로 고정 ¦ high clipping
A2750P_SYSTEM_Accura_2750P_System_Setup_eeprom_save_enable_time_low_clip | TRUE | A2700 | 54911 | 54912 | 1 | uint16 | 4 | 5 | 5 | 100 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 54910 must be preset before run ¦ access doc addr 54911 ¦ source map row 1259 ¦ eeprom에 저장하기 위해 필요한 시간 (5-100) ¦ low clipping
A2750P_SYSTEM_Accura_2750P_System_Setup_eeprom_save_enable_time_high_clip | TRUE | A2700 | 54911 | 54912 | 1 | uint16 | 101 | 100 | 5 | 100 |  |  | 1 | 500 | 5 | TRUE | A2750P ID=1 assumed; ID doc addr 54910 must be preset before run ¦ access doc addr 54911 ¦ source map row 1259 ¦ eeprom에 저장하기 위해 필요한 시간 (5-100) ¦ high clipping
A2750P_SYSTEM_Accura_2750P_System_Setup_charging_reference_voltage_low_clip | TRUE | A2700 | 54911 | 54913 | 1 | uint16 | 399 | 400 | 400 | 550 |  |  | 1 | 500 | 490 | TRUE | A2750P ID=1 assumed; ID doc addr 54910 must be preset before run ¦ access doc addr 54911 ¦ source map row 1260 ¦ 충전을 판단하는 기준 전압 설정 (400-550) ¦ low clipping
A2750P_SYSTEM_Accura_2750P_System_Setup_charging_reference_voltage_high_clip | TRUE | A2700 | 54911 | 54913 | 1 | uint16 | 551 | 550 | 400 | 550 |  |  | 1 | 500 | 490 | TRUE | A2750P ID=1 assumed; ID doc addr 54910 must be preset before run ¦ access doc addr 54911 ¦ source map row 1260 ¦ 충전을 판단하는 기준 전압 설정 (400-550) ¦ high clipping

## README
Clipping Test Excel Format - A2750P
목적 | A2750P 모듈 설정값에 범위 밖 raw 값을 write했을 때 min/max clipping되는지 검증
주소 기준 | doc_addr 컬럼은 Modbus Map 문서 주소 그대로 입력. 실행 코드에서 내부적으로 -1 적용
ID 전제 | A2750P ID는 1번으로 사전 설정되어 있다고 가정. 현재 clipping runner는 ID register와 access register를 별도로 동시에 write하지 않음
대상 블록 | A2750 Common UI, A2750P UI, A2750P Measurement, Protection A2750P[C], A2750P System
제외 항목 | 에너지 누적값, 명령/리셋, 문자열, 전용 모듈(D/LC/DC/IRM/DO), 정격별 범위가 여러 개인 항목
write_value | 일부러 범위 밖으로 넣는 raw register 값
expected_value | commit 후 readback에서 기대하는 clipping된 raw register 값
valid_low/high | expected_value는 정확값, valid_low/high는 허용 raw 범위
restore_after | TRUE면 테스트 후 restore_value로 원복
product 컬럼 | A2750P는 현재 UI 제품군상 A2700 계열이므로 A2700으로 작성
생성 기준 | 명확한 단일 integer raw range만 자동 생성. 총 131개 케이스
원본 맵 | config/modbus_map/Accura 2700_2750 Modbus Map(VER.2025).xlsx

## Excluded
source_row | category | subcategory | addr_doc | name | reason | description
724 | User Interface Setup | Accura 2750 Common Interface | 51234 | RUN confirm window of A2700D[W] | no single integer raw range | 0: Disable 1: Enable
725 | User Interface Setup | Accura 2750 Common Interface | 51235 | STOP confirm window of A2700D[W] | no single integer raw range | 0: Disable 1: Enable
726 | User Interface Setup | Accura 2750 Common Interface | 51236 | STOP extension time | low bound is 0; uint register cannot write below 0 safely | STOP extension time 범위 : 0 ~ 20 (단위 : 0.1초)
727 | User Interface Setup | Accura 2750 Common Interface | 51237 | Hide Refusal Display | no single integer raw range | 제어명령 거절 화면에 대한 표시 여부 0: display 1: no-display
733 | User Interface Setup | Accura 2750P User Interface | 51245 | LCD display control | no single integer raw range | Display mode 0: Remote control, 1: Self rotation
734 | User Interface Setup | Accura 2750P User Interface | 51246 | Page of remote control | no single integer raw range | Display page of remote control 0: ID, 1:A-phase, 2: B-phase, 3: C-phase, 4: ABC-phase, 5: Energy, 6: ZCT current, 7: Current rate, 8: TCU
788 | Measurement Setup | A2750P Measurement Setup | 51393 | Load type | no single integer raw range | 모터 부하 타입 0: 3P 1: 1P 1P 설정 시 계전요소 PSR, POCR, UBCR 미지원 기동모드 Reverse, Two-Speed, Two-Step 미지원
790 | Measurement Setup | A2750P Measurement Setup | 51395 | Voltage phase selection | no single integer raw range | Load type이 1P일 경우의 전압상 선택 0000 (0h) : A-B, 0001 (1h) : B-C, 0010 (2h) : C-A 0011 (3h) : B-A, 0100 (4h) : C-B, 0101 (5h) : A-C 1000 (8h) : A-N, 1001 (9h) : B-N, 1010 (Ah) : C-N 1011 (Bh) : N-A, 1100 (Ch) : N-B, 1101 (Dh) : N-C Load type이 3P일 경우의 전압상 선택(매뉴얼 비공개) 0000 (0h) : A-B-C, 0001 (1h) : A-C-B, 0010 (2h) : B-A-C 0011 (3h) : B-C-A, 0100 (4h) : C-A-B, 0101 (5h) : C-B-A
793 | Measurement Setup | A2750P Measurement Setup | 51399 | Current direction | no single integer raw range | 전류 방향 0: Normal 1: Reverse
794 | Measurement Setup | A2750P Measurement Setup | 51400 | Full load current 1st | no single integer raw range | 최대 부하 전류 ACB module 범위 : 50(0.50A) ~ 500(5.00A) 기본값 : 500(5,00A) CT5A module 범위 : 50(0.50A) ~ 500(5.00A) 기본값 : 500(5.00A) 30A module 범위 : 30(3.0A) ~ 300(30.0A) 기본값 : 300(30.0A) 100A module 범위 : 100(10.0A) ~ 1000(100.0A) 기본값 : 1000(100.0A) 160A module 범위 : 160(16.0A)~ 1600(160.0A) 기본값 : 1600(160.0A) 250A module 범위 : 250(25.0A) ~ 2500(250.0A) 기본값 : 2500(250.0A) 400A module 범위 : 400(40.0A) ~ 4000(400.0A) 기본값 : 4000(400.0A)
795 | Measurement Setup | A2750P Measurement Setup | 51401 | Full load current 2nd | no single integer raw range | 최대 부하 전류 ACB module 범위 : 50(0.50A) ~ 500(5.00A) 기본값 : 500(5,00A) CT5A module 범위 : 50(0.50A) ~ 500(5.00A) 기본값 : 500(5.00A) 30A module 범위 : 30(3.0A) ~ 300(30.0A) 기본값 : 300(30.0A) 100A module 범위 : 100(10.0A) ~ 1000(100.0A) 기본값 : 1000(100.0A) 160A module 범위 : 160(16.0A)~ 1600(160.0A) 기본값 : 1600(160.0A) 250A module 범위 : 250(25.0A) ~ 2500(250.0A) 기본값 : 2500(250.0A) 400A module 범위 : 400(40.0A) ~ 4000(400.0A) 기본값 : 4000(400.0A)
796 | Measurement Setup | A2750P Measurement Setup | 51402 | Minimum measured current | no single integer raw range | 최소 계측 전류 ACB module 범위 : 1 ~ 100 기본값 : 50(50mA) CT5A module 범위 : 1 ~ 100 기본값 : 50(50mA) 30A module 범위 : 1 ~ 600 기본값 : 300(300mA) 100A module 범위 : 1 ~ 2000 기본값 : 1000(1000mA) 160A module 범위 : 1 ~ 3200 기본값 : 1600(1600mA) 250A module 범위 : 1 ~ 5000 기본값 : 2500(2500mA) 400A module 범위 : 1 ~ 8000 기본값 : 4000(4000mA)
801 | Measurement Setup | A2750P Measurement Setup | 51407 | Start-to-run condition | no single integer raw range | 0: Normal - start-to-run threshold 조건과 start-to-run time delay 조건 중 하나라도 만족하면 운전으로 진입 1: Time only - start-to-run time delay 조건만 만족하면 운전으로 진입
819 | Protection A2750P[C] Setup | THR | 51543 | Fault function | no single integer raw range | Fault 활성화 여부 0: Disable 1: Enable
820 | Protection A2750P[C] Setup | THR | 51544 | Alarm function | no single integer raw range | Alarm 활성화 여부 0 : Disable 1: Alarm 2: Latched Alarm
824 | Protection A2750P[C] Setup | THR | 51548 | Current unbalance factor | low bound is 0; uint register cannot write below 0 safely | Current unabalance factor 0(0.0) ~ 100(10.0)
825 | Protection A2750P[C] Setup | THR | 51549 | THR input current | no single integer raw range | THR 입력 전류 0: I max 1: I average
826 | Protection A2750P[C] Setup | THR | 51550 | Cooling mode | no single integer raw range | 냉각 기준 판단 0: Time 1: Restart level
828 | Protection A2750P[C] Setup | THR | 51552 | Pause time | low bound is 0; uint register cannot write below 0 safely | Pause time. Cooling mode가 Time으로 설정된 경우에만 사용 0 ~ 9999
830 | Protection A2750P[C] Setup | OCR | 51554 | Fault function | no single integer raw range | Fault 활성화 여부 0: Disable 1: Enable
831 | Protection A2750P[C] Setup | OCR | 51555 | Alarm function | no single integer raw range | Alarm 활성화 여부 0 : Disable 1: Alarm 2: Latched Alarm
832 | Protection A2750P[C] Setup | OCR | 51556 | Fault threshold | no single integer raw range | Fault 기준 90 ~ 600 % ACB module : 90 ~ 1000%
833 | Protection A2750P[C] Setup | OCR | 51557 | Fault time delay | no single integer raw range | Fault 판단 지연 시간 1(0.1s) ~ 9999(999.9s) ACB module : 5(0.05s) ~ 9999(99.99s)
836 | Protection A2750P[C] Setup | POCR | 51560 | Fault function | no single integer raw range | Fault 활성화 여부 0: Disable 1: Enable
837 | Protection A2750P[C] Setup | POCR | 51561 | Alarm function | no single integer raw range | Alarm 활성화 여부 0 : Disable 1: Alarm 2: Latched Alarm
841 | Protection A2750P[C] Setup | POCR | 51565 | Startup time delay | low bound is 0; uint register cannot write below 0 safely | Startup 지연 시간 0(0.0ec) ~ 50(5.0sec)
842 | Protection A2750P[C] Setup | POCR | 51566 | Current calculation method | no single integer raw range | 전류 계산 방법 0: Phase Unbalance 1: Zero Sequence Unabalance
843 | Protection A2750P[C] Setup | PSR | 51567 | Fault function | no single integer raw range | Fault 활성화 여부 0: Disable 1: Enable
844 | Protection A2750P[C] Setup | UBCR | 51568 | Fault function | no single integer raw range | Fault 활성화 여부 0: Disable 1: Enable
845 | Protection A2750P[C] Setup | UBCR | 51569 | Alarm function | no single integer raw range | Alarm 활성화 여부 0 : Disable 1: Alarm 2: Latched Alarm
850 | Protection A2750P[C] Setup | UBCR | 51574 | Startup time delay | low bound is 0; uint register cannot write below 0 safely | Startup 지연 시간 0(0.0ec) ~ 50(5.0sec)
851 | Protection A2750P[C] Setup | UBCR | 51575 | Current calculation method | no single integer raw range | 전류 계산 방법 0: Phase Unbalance 1: Zero Sequence Unabalance
853 | Protection A2750P[C] Setup | JAM | 51577 | Fault function | no single integer raw range | Fault 활성화 여부 0: Disable 1: Enable
854 | Protection A2750P[C] Setup | JAM | 51578 | Alarm function | no single integer raw range | Alarm 활성화 여부 0 : Disable 1: Alarm 2: Latched Alarm
859 | Protection A2750P[C] Setup | JAM | 51583 | Current calculation method | no single integer raw range | 전류 계산 방법 0: I max 1: I average
860 | Protection A2750P[C] Setup | GR[ZCT] | 51584 | Fault function | no single integer raw range | Fault 활성화 여부 0: Disable 1: Enable
861 | Protection A2750P[C] Setup | GR[ZCT] | 51585 | Alarm function | no single integer raw range | Alarm 활성화 여부 0 : Disable 1: Alarm 2: Latched Alarm
866 | Protection A2750P[C] Setup | GR[ZCT] | 51590 | Startup blocking | no single integer raw range | Startup blocking 0: Disable 1: Enable
868 | Protection A2750P[C] Setup | GR[CT] | 51592 | Fault function | no single integer raw range | Fault 활성화 여부 0: Disable 1: Enable
869 | Protection A2750P[C] Setup | GR[CT] | 51593 | Alarm function | no single integer raw range | Alarm 활성화 여부 0 : Disable 1: Alarm 2: Latched Alarm
870 | Protection A2750P[C] Setup | GR[CT] | 51594 | Fault threshold | no single integer raw range | Fault 기준 Accura 2750PC-ACB 25(0.25A) ~ 200(2.00A) Accura 2750PC-5A 20(20A) ~ 30(30A) Accura 2750PC-30A 20(20A) ~ 30(30A) Accura 2750PC-100A 20(20A) ~ 100(100A) Accura 2750PC-160A 20(20A) ~ 160(160A) Accura 2750PC-250A 20(20A) ~ 250(250A) Accura 2750PC-400A 20(20A) ~ 400(400A)
872 | Protection A2750P[C] Setup | GR[CT] | 51596 | Alarm threshold | no single integer raw range | Alarm 기준 Accura 2750PC-ACB 25(0.25A) ~ 200(2.00A) Accura 2750PC-5A 20(20A) ~ 30(30A) Accura 2750PC-30A 20(20A) ~ 30(30A) Accura 2750PC-100A 20(20A) ~ 100(100A) Accura 2750PC-160A 20(20A) ~ 160(160A) Accura 2750PC-250A 20(20A) ~ 250(250A) Accura 2750PC-400A 20(20A) ~ 400(400A)
874 | Protection A2750P[C] Setup | GR[CT] | 51598 | Startup blocking | no single integer raw range | Startup blocking 0 : Disable 1 : Enable
876 | Protection A2750P[C] Setup | UCR | 51600 | Fault function | no single integer raw range | Fault 활성화 여부 0: Disable 1: Enable
877 | Protection A2750P[C] Setup | UCR | 51601 | Alarm function | no single integer raw range | Alarm 활성화 여부 0 : Disable 1: Alarm 2: Latched Alarm
882 | Protection A2750P[C] Setup | LSR | 51606 | Fault function | no single integer raw range | Fault 활성화 여부 0: Disable 1: Enable
883 | Protection A2750P[C] Setup | LSR | 51607 | Alarm function | no single integer raw range | Alarm 활성화 여부 0: Disable 2: Latched Alarm
884 | Protection A2750P[C] Setup | MC Supervision | 51608 | Fault function | no single integer raw range | Fault 활성화 여부 0: Disable 1: Enable
887 | Protection A2750P[C] Setup | IOCR | 51611 | Fault function | no single integer raw range | Fault 활성화 여부 0: Disable 1: Enable
888 | Protection A2750P[C] Setup | IOCR | 51612 | Fault threshold | no single integer raw range | Fault 기준 5A : 50(5.0A) ~ 400(40.0A) 30A : 300(30.0A) ~ 2400(240.0A) 100A : 1000(100.0A) ~ 8000(800.0A) 160A : 1600(160.0A) ~ 12800(1280.0A) 250A : 2500(250.0A) ~ 20000(2000.0A) 400A : 4000(400.0A) ~ 32000(3200.0A) ACB : 200~1600%FLC
891 | Protection A2750P[C] Setup | PSR | 51615 | Run enable | no single integer raw range | Run enable 0 : Disable, 1 : Enable
893 | Protection A2750P[C] Setup | UVR | 51617 | Fault function | no single integer raw range | Fault 활성화 여부 0: Disable 1: Enable
894 | Protection A2750P[C] Setup | UVR | 51618 | Alarm function | no single integer raw range | Alarm 활성화 여부 0: Disable 1: Enable 2: Latched Alarm
895 | Protection A2750P[C] Setup | UVR | 51619 | Fault threshold | no single integer raw range | 70% ~ 99%
897 | Protection A2750P[C] Setup | UVR | 51621 | Alarm threshold | no single integer raw range | 70% ~ 99%
899 | Protection A2750P[C] Setup | LT.OCR | 51623 | Fault Enable | no single integer raw range | Fault 활성화 여부 0: Disable 1: Enable
902 | Protection A2750P[C] Setup | OCR (extenstion) | 51626 | OCR Startup blocking | no single integer raw range | 0 : Disable 1 : Enable
903 | Protection A2750P[C] Setup | I.OCR (extension) | 51627 | I.OCR Alarm Function | no single integer raw range | 0: Disable, 1: Enable
904 | Protection A2750P[C] Setup | I.OCR (extension) | 51628 | I.OCR Alarm Threshold | no single integer raw range | Alarm 기준 5A : 50(5.0A) ~ 400(40.0A) 30A : 300(30.0A) ~ 2400(240.0A) 100A : 1000(100.0A) ~ 8000(800.0A) 160A : 1600(160.0A) ~ 12800(1280.0A) 250A : 2500(250.0A) ~ 20000(2000.0A) 400A : 4000(400.0A) ~ 32000(3200.0A) ACB : 200~1600%FLC
906 | Protection A2750P[C] Setup | I.OCR (extension) | 51630 | OCR Curve type | no single integer raw range | 0: Definite time 1: IEC A (IEC Inverse) 2: IEC B (IEC Very Inverse) 3: IEC C (IEC Extremely Inverse) 4: LTI (LONG TIME Inverse)
907 | Protection A2750P[C] Setup | I.OCR (extension) | 51631 | OCR Time multiplier | no single integer raw range | 0.05 ~ 10.00